## Worksheet
Parameter | Unit 1 | Unit 2
Pumps disabled during the experiment | 1, 5 | 3, 5
Backup pump | 3 | 1
State of HPH-5, 6 | Disabled | Enabled
Reactor power, % | 97.8 | 99.9
Average thermal power, MW | 3132 | 3197
TG power,% | 92 | 94.9
Automatic power controller (APC) operating mode | T | T
Turbine governor electrical part (TGEP) operating mode | PC | PC
Above-core pressure, MPa | 15.87 | 15.94
Average hot leg temperature, °C | 326.2 | 326
Average cold leg temperature, °C | 294.8 | 295.3
Pressurizer level, m | 7.9 | 7.8
Average SG level, m | 2.71 | 2.7
LPH-2 water level, m | 3.44 | 3.34
LPH-4 water level, m | 0.158 | 0.286
Deaerator water level, m | 2.63 | 3.11
Total pump head flow rate, m3/h | 6298 | 7162
Pump head pressure, MPa | 9.3 | 8.7
Average main level controller (MLC) opening in the steam generators (SG), % | 39 | 60
Average startup level controller (SLC) opening in the steam generators (SG), % | 28 | 27
Total SG feed water flow rate, m3/h | 6403 | 7698
Average SG inlet feed water temperature, °C | 172 | 227
Main steam header (MSH) pressure, MPa | 6.8 | 6.9
Fast acting steam dump valve with discharge to the deaerator (BRU-D) opening, % | 5 | 0
Average turbine stop-control valve (SCV) opening,% | 29 | 46
Fast acting steam dump valve with discharge to the auxiliary header (BRU-SN) opening, % | 12 | 0